## 692-9-C3
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Extremely Inverse I.E.C. (C3) (TCC 692-9-C3) | [9 empty] | Extremely Inverse I.E.C. (C3) (TCC 692-9-C3) | [9 empty] | Extremely Inverse I.E.C. (C3) (TCC 692-9-C3)
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.05 |  | Time Dial = 0.1 |  | Time Dial = 0.2 |  | Time Dial = 0.3 |  | Time Dial = 0.4 |  | Time Dial = 0.5 |  | Time Dial = 0.6 |  | Time Dial = 0.7 |  | Time Dial = 0.8 |  | Time Dial = 0.9 |  | Time Dial = 1.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 3.2 | 1.5 | 6.4 | 1.5 | 12.8 | 1.5 | 19.2 | 1.5 | 25.6 | 1.5 | 32 | 1.5 | 38.4 | 1.5 | 44.8 | 1.5 | 51.2 | 1.5 | 57.6 | 1.5 | 64
1.6 | 2.5641 | 1.6 | 5.1282 | 1.6 | 10.2564 | 1.6 | 15.3846 | 1.6 | 20.5128 | 1.6 | 25.641 | 1.6 | 30.7692 | 1.6 | 35.8974 | 1.6 | 41.0256 | 1.6 | 46.1538 | 1.6 | 51.2821
1.7 | 2.1164 | 1.7 | 4.2328 | 1.7 | 8.4656 | 1.7 | 12.6984 | 1.7 | 16.9312 | 1.7 | 21.164 | 1.7 | 25.3968 | 1.7 | 29.6296 | 1.7 | 33.8624 | 1.7 | 38.0952 | 1.7 | 42.328
1.8 | 1.7857 | 1.8 | 3.5714 | 1.8 | 7.1429 | 1.8 | 10.7143 | 1.8 | 14.2857 | 1.8 | 17.8571 | 1.8 | 21.4286 | 1.8 | 25 | 1.8 | 28.5714 | 1.8 | 32.1429 | 1.8 | 35.7143
1.9 | 1.5326 | 1.9 | 3.0651 | 1.9 | 6.1303 | 1.9 | 9.1954 | 1.9 | 12.2605 | 1.9 | 15.3257 | 1.9 | 18.3908 | 1.9 | 21.4559 | 1.9 | 24.5211 | 1.9 | 27.5862 | 1.9 | 30.6513
2 | 1.3333 | 2 | 2.6667 | 2 | 5.3333 | 2 | 8 | 2 | 10.6667 | 2 | 13.3333 | 2 | 16 | 2 | 18.6667 | 2 | 21.3333 | 2 | 24 | 2 | 26.6667
2.1 | 1.173 | 2.1 | 2.346 | 2.1 | 4.6921 | 2.1 | 7.0381 | 2.1 | 9.3842 | 2.1 | 11.7302 | 2.1 | 14.0762 | 2.1 | 16.4223 | 2.1 | 18.7683 | 2.1 | 21.1144 | 2.1 | 23.4604
2.2 | 1.0417 | 2.2 | 2.0833 | 2.2 | 4.1667 | 2.2 | 6.25 | 2.2 | 8.3333 | 2.2 | 10.4167 | 2.2 | 12.5 | 2.2 | 14.5833 | 2.2 | 16.6667 | 2.2 | 18.75 | 2.2 | 20.8333
2.3 | 0.9324 | 2.3 | 1.8648 | 2.3 | 3.7296 | 2.3 | 5.5944 | 2.3 | 7.4592 | 2.3 | 9.324 | 2.3 | 11.1888 | 2.3 | 13.0536 | 2.3 | 14.9184 | 2.3 | 16.7832 | 2.3 | 18.648
2.4 | 0.84034 | 2.4 | 1.6807 | 2.4 | 3.3613 | 2.4 | 5.042 | 2.4 | 6.7227 | 2.4 | 8.4034 | 2.4 | 10.084 | 2.4 | 11.7647 | 2.4 | 13.4454 | 2.4 | 15.1261 | 2.4 | 16.8067
2.5 | 0.7619 | 2.5 | 1.5238 | 2.5 | 3.0476 | 2.5 | 4.5714 | 2.5 | 6.0952 | 2.5 | 7.619 | 2.5 | 9.1429 | 2.5 | 10.6667 | 2.5 | 12.1905 | 2.5 | 13.7143 | 2.5 | 15.2381
2.6 | 0.69444 | 2.6 | 1.3889 | 2.6 | 2.7778 | 2.6 | 4.1667 | 2.6 | 5.5556 | 2.6 | 6.9444 | 2.6 | 8.3333 | 2.6 | 9.7222 | 2.6 | 11.1111 | 2.6 | 12.5 | 2.6 | 13.8889
2.7 | 0.63593 | 2.7 | 1.2719 | 2.7 | 2.5437 | 2.7 | 3.8156 | 2.7 | 5.0874 | 2.7 | 6.3593 | 2.7 | 7.6312 | 2.7 | 8.903 | 2.7 | 10.1749 | 2.7 | 11.4467 | 2.7 | 12.7186
2.8 | 0.5848 | 2.8 | 1.1696 | 2.8 | 2.3392 | 2.8 | 3.5088 | 2.8 | 4.6784 | 2.8 | 5.848 | 2.8 | 7.0175 | 2.8 | 8.1871 | 2.8 | 9.3567 | 2.8 | 10.5263 | 2.8 | 11.6959
2.9 | 0.53981 | 2.9 | 1.0796 | 2.9 | 2.1592 | 2.9 | 3.2389 | 2.9 | 4.3185 | 2.9 | 5.3981 | 2.9 | 6.4777 | 2.9 | 7.5574 | 2.9 | 8.637 | 2.9 | 9.7166 | 2.9 | 10.7962
3 | 0.5 | 3 | 1 | 3 | 2 | 3 | 3 | 3 | 4 | 3 | 5 | 3 | 6 | 3 | 7 | 3 | 8 | 3 | 9 | 3 | 10
3.1 | 0.46458 | 3.1 | 0.92915 | 3.1 | 1.8583 | 3.1 | 2.7875 | 3.1 | 3.7166 | 3.1 | 4.6458 | 3.1 | 5.5749 | 3.1 | 6.5041 | 3.1 | 7.4332 | 3.1 | 8.3624 | 3.1 | 9.2915
3.2 | 0.4329 | 3.2 | 0.8658 | 3.2 | 1.7316 | 3.2 | 2.5974 | 3.2 | 3.4632 | 3.2 | 4.329 | 3.2 | 5.1948 | 3.2 | 6.0606 | 3.2 | 6.9264 | 3.2 | 7.7922 | 3.2 | 8.658
3.3 | 0.40445 | 3.3 | 0.8089 | 3.3 | 1.6178 | 3.3 | 2.4267 | 3.3 | 3.2356 | 3.3 | 4.0445 | 3.3 | 4.8534 | 3.3 | 5.6623 | 3.3 | 6.4712 | 3.3 | 7.2801 | 3.3 | 8.089
3.4 | 0.37879 | 3.4 | 0.75758 | 3.4 | 1.5152 | 3.4 | 2.2727 | 3.4 | 3.0303 | 3.4 | 3.7879 | 3.4 | 4.5455 | 3.4 | 5.303 | 3.4 | 6.0606 | 3.4 | 6.8182 | 3.4 | 7.5758
3.5 | 0.35556 | 3.5 | 0.71111 | 3.5 | 1.4222 | 3.5 | 2.1333 | 3.5 | 2.8444 | 3.5 | 3.5556 | 3.5 | 4.2667 | 3.5 | 4.9778 | 3.5 | 5.6889 | 3.5 | 6.4 | 3.5 | 7.1111
3.6 | 0.33445 | 3.6 | 0.6689 | 3.6 | 1.3378 | 3.6 | 2.0067 | 3.6 | 2.6756 | 3.6 | 3.3445 | 3.6 | 4.0134 | 3.6 | 4.6823 | 3.6 | 5.3512 | 3.6 | 6.0201 | 3.6 | 6.689
3.7 | 0.31521 | 3.7 | 0.63042 | 3.7 | 1.2608 | 3.7 | 1.8913 | 3.7 | 2.5217 | 3.7 | 3.1521 | 3.7 | 3.7825 | 3.7 | 4.4129 | 3.7 | 5.0433 | 3.7 | 5.6738 | 3.7 | 6.3042
3.8 | 0.29762 | 3.8 | 0.59524 | 3.8 | 1.1905 | 3.8 | 1.7857 | 3.8 | 2.381 | 3.8 | 2.9762 | 3.8 | 3.5714 | 3.8 | 4.1667 | 3.8 | 4.7619 | 3.8 | 5.3571 | 3.8 | 5.9524
3.9 | 0.28149 | 3.9 | 0.56298 | 3.9 | 1.126 | 3.9 | 1.689 | 3.9 | 2.2519 | 3.9 | 2.8149 | 3.9 | 3.3779 | 3.9 | 3.9409 | 3.9 | 4.5039 | 3.9 | 5.0669 | 3.9 | 5.6298
4 | 0.26667 | 4 | 0.53333 | 4 | 1.0667 | 4 | 1.6 | 4 | 2.1333 | 4 | 2.6667 | 4 | 3.2 | 4 | 3.7333 | 4 | 4.2667 | 4 | 4.8 | 4 | 5.3333
4.1 | 0.253 | 4.1 | 0.50601 | 4.1 | 1.012 | 4.1 | 1.518 | 4.1 | 2.024 | 4.1 | 2.53 | 4.1 | 3.0361 | 4.1 | 3.5421 | 4.1 | 4.0481 | 4.1 | 4.5541 | 4.1 | 5.0601
4.2 | 0.24038 | 4.2 | 0.48077 | 4.2 | 0.96154 | 4.2 | 1.4423 | 4.2 | 1.9231 | 4.2 | 2.4038 | 4.2 | 2.8846 | 4.2 | 3.3654 | 4.2 | 3.8462 | 4.2 | 4.3269 | 4.2 | 4.8077
4.3 | 0.2287 | 4.3 | 0.4574 | 4.3 | 0.91481 | 4.3 | 1.3722 | 4.3 | 1.8296 | 4.3 | 2.287 | 4.3 | 2.7444 | 4.3 | 3.2018 | 4.3 | 3.6592 | 4.3 | 4.1166 | 4.3 | 4.574
4.4 | 0.21786 | 4.4 | 0.43573 | 4.4 | 0.87146 | 4.4 | 1.3072 | 4.4 | 1.7429 | 4.4 | 2.1786 | 4.4 | 2.6144 | 4.4 | 3.0501 | 4.4 | 3.4858 | 4.4 | 3.9216 | 4.4 | 4.3573
4.5 | 0.20779 | 4.5 | 0.41558 | 4.5 | 0.83117 | 4.5 | 1.2468 | 4.5 | 1.6623 | 4.5 | 2.0779 | 4.5 | 2.4935 | 4.5 | 2.9091 | 4.5 | 3.3247 | 4.5 | 3.7403 | 4.5 | 4.1558
4.6 | 0.19841 | 4.6 | 0.39683 | 4.6 | 0.79365 | 4.6 | 1.1905 | 4.6 | 1.5873 | 4.6 | 1.9841 | 4.6 | 2.381 | 4.6 | 2.7778 | 4.6 | 3.1746 | 4.6 | 3.5714 | 4.6 | 3.9683
4.7 | 0.18966 | 4.7 | 0.37933 | 4.7 | 0.75865 | 4.7 | 1.138 | 4.7 | 1.5173 | 4.7 | 1.8966 | 4.7 | 2.276 | 4.7 | 2.6553 | 4.7 | 3.0346 | 4.7 | 3.4139 | 4.7 | 3.7933
4.8 | 0.18149 | 4.8 | 0.36298 | 4.8 | 0.72595 | 4.8 | 1.0889 | 4.8 | 1.4519 | 4.8 | 1.8149 | 4.8 | 2.1779 | 4.8 | 2.5408 | 4.8 | 2.9038 | 4.8 | 3.2668 | 4.8 | 3.6298
4.9 | 0.17384 | 4.9 | 0.34767 | 4.9 | 0.69535 | 4.9 | 1.043 | 4.9 | 1.3907 | 4.9 | 1.7384 | 4.9 | 2.086 | 4.9 | 2.4337 | 4.9 | 2.7814 | 4.9 | 3.1291 | 4.9 | 3.4767
5 | 0.16667 | 5 | 0.33333 | 5 | 0.66667 | 5 | 1 | 5 | 1.3333 | 5 | 1.6667 | 5 | 2 | 5 | 2.3333 | 5 | 2.6667 | 5 | 3 | 5 | 3.3333
5.1 | 0.15994 | 5.1 | 0.31987 | 5.1 | 0.63974 | 5.1 | 0.95962 | 5.1 | 1.2795 | 5.1 | 1.5994 | 5.1 | 1.9192 | 5.1 | 2.2391 | 5.1 | 2.559 | 5.1 | 2.8788 | 5.1 | 3.1987
5.2 | 0.15361 | 5.2 | 0.30722 | 5.2 | 0.61444 | 5.2 | 0.92166 | 5.2 | 1.2289 | 5.2 | 1.5361 | 5.2 | 1.8433 | 5.2 | 2.1505 | 5.2 | 2.4578 | 5.2 | 2.765 | 5.2 | 3.0722
5.3 | 0.14766 | 5.3 | 0.29531 | 5.3 | 0.59062 | 5.3 | 0.88594 | 5.3 | 1.1812 | 5.3 | 1.4766 | 5.3 | 1.7719 | 5.3 | 2.0672 | 5.3 | 2.3625 | 5.3 | 2.6578 | 5.3 | 2.9531
5.4 | 0.14205 | 5.4 | 0.28409 | 5.4 | 0.56818 | 5.4 | 0.85227 | 5.4 | 1.1364 | 5.4 | 1.4205 | 5.4 | 1.7045 | 5.4 | 1.9886 | 5.4 | 2.2727 | 5.4 | 2.5568 | 5.4 | 2.8409
5.5 | 0.13675 | 5.5 | 0.2735 | 5.5 | 0.54701 | 5.5 | 0.82051 | 5.5 | 1.094 | 5.5 | 1.3675 | 5.5 | 1.641 | 5.5 | 1.9145 | 5.5 | 2.188 | 5.5 | 2.4615 | 5.5 | 2.735
5.6 | 0.13175 | 5.6 | 0.2635 | 5.6 | 0.52701 | 5.6 | 0.79051 | 5.6 | 1.054 | 5.6 | 1.3175 | 5.6 | 1.581 | 5.6 | 1.8445 | 5.6 | 2.108 | 5.6 | 2.3715 | 5.6 | 2.635
5.7 | 0.12702 | 5.7 | 0.25405 | 5.7 | 0.5081 | 5.7 | 0.76215 | 5.7 | 1.0162 | 5.7 | 1.2702 | 5.7 | 1.5243 | 5.7 | 1.7783 | 5.7 | 2.0324 | 5.7 | 2.2864 | 5.7 | 2.5405
5.8 | 0.12255 | 5.8 | 0.2451 | 5.8 | 0.4902 | 5.8 | 0.73529 | 5.8 | 0.98039 | 5.8 | 1.2255 | 5.8 | 1.4706 | 5.8 | 1.7157 | 5.8 | 1.9608 | 5.8 | 2.2059 | 5.8 | 2.451
5.9 | 0.11831 | 5.9 | 0.23662 | 5.9 | 0.47323 | 5.9 | 0.70985 | 5.9 | 0.94647 | 5.9 | 1.1831 | 5.9 | 1.4197 | 5.9 | 1.6563 | 5.9 | 1.8929 | 5.9 | 2.1295 | 5.9 | 2.3662
6 | 0.11429 | 6 | 0.22857 | 6 | 0.45714 | 6 | 0.68571 | 6 | 0.91429 | 6 | 1.1429 | 6 | 1.3714 | 6 | 1.6 | 6 | 1.8286 | 6 | 2.0571 | 6 | 2.2857
6.1 | 0.11047 | 6.1 | 0.22093 | 6.1 | 0.44187 | 6.1 | 0.6628 | 6.1 | 0.88373 | 6.1 | 1.1047 | 6.1 | 1.3256 | 6.1 | 1.5465 | 6.1 | 1.7675 | 6.1 | 1.9884 | 6.1 | 2.2093
6.2 | 0.10684 | 6.2 | 0.21368 | 6.2 | 0.42735 | 6.2 | 0.64103 | 6.2 | 0.8547 | 6.2 | 1.0684 | 6.2 | 1.2821 | 6.2 | 1.4957 | 6.2 | 1.7094 | 6.2 | 1.9231 | 6.2 | 2.1368
6.3 | 0.10339 | 6.3 | 0.20677 | 6.3 | 0.41354 | 6.3 | 0.62032 | 6.3 | 0.82709 | 6.3 | 1.0339 | 6.3 | 1.2406 | 6.3 | 1.4474 | 6.3 | 1.6542 | 6.3 | 1.8609 | 6.3 | 2.0677
6.4 | 0.1001 | 6.4 | 0.2002 | 6.4 | 0.4004 | 6.4 | 0.6006 | 6.4 | 0.8008 | 6.4 | 1.001 | 6.4 | 1.2012 | 6.4 | 1.4014 | 6.4 | 1.6016 | 6.4 | 1.8018 | 6.4 | 2.002
6.5 | 0.09697 | 6.5 | 0.19394 | 6.5 | 0.38788 | 6.5 | 0.58182 | 6.5 | 0.77576 | 6.5 | 0.9697 | 6.5 | 1.1636 | 6.5 | 1.3576 | 6.5 | 1.5515 | 6.5 | 1.7455 | 6.5 | 1.9394
6.6 | 0.093985 | 6.6 | 0.18797 | 6.6 | 0.37594 | 6.6 | 0.56391 | 6.6 | 0.75188 | 6.6 | 0.93985 | 6.6 | 1.1278 | 6.6 | 1.3158 | 6.6 | 1.5038 | 6.6 | 1.6917 | 6.6 | 1.8797
6.7 | 0.091137 | 6.7 | 0.18227 | 6.7 | 0.36455 | 6.7 | 0.54682 | 6.7 | 0.7291 | 6.7 | 0.91137 | 6.7 | 1.0936 | 6.7 | 1.2759 | 6.7 | 1.4582 | 6.7 | 1.6405 | 6.7 | 1.8227
6.8 | 0.088417 | 6.8 | 0.17683 | 6.8 | 0.35367 | 6.8 | 0.5305 | 6.8 | 0.70734 | 6.8 | 0.88417 | 6.8 | 1.061 | 6.8 | 1.2378 | 6.8 | 1.4147 | 6.8 | 1.5915 | 6.8 | 1.7683
6.9 | 0.085818 | 6.9 | 0.17164 | 6.9 | 0.34327 | 6.9 | 0.51491 | 6.9 | 0.68655 | 6.9 | 0.85818 | 6.9 | 1.0298 | 6.9 | 1.2015 | 6.9 | 1.3731 | 6.9 | 1.5447 | 6.9 | 1.7164
7 | 0.083333 | 7 | 0.16667 | 7 | 0.33333 | 7 | 0.5 | 7 | 0.66667 | 7 | 0.83333 | 7 | 1 | 7 | 1.1667 | 7 | 1.3333 | 7 | 1.5 | 7 | 1.6667
7.1 | 0.080955 | 7.1 | 0.16191 | 7.1 | 0.32382 | 7.1 | 0.48573 | 7.1 | 0.64764 | 7.1 | 0.80955 | 7.1 | 0.97146 | 7.1 | 1.1334 | 7.1 | 1.2953 | 7.1 | 1.4572 | 7.1 | 1.6191
7.2 | 0.078678 | 7.2 | 0.15736 | 7.2 | 0.31471 | 7.2 | 0.47207 | 7.2 | 0.62943 | 7.2 | 0.78678 | 7.2 | 0.94414 | 7.2 | 1.1015 | 7.2 | 1.2589 | 7.2 | 1.4162 | 7.2 | 1.5736
7.3 | 0.076496 | 7.3 | 0.15299 | 7.3 | 0.30599 | 7.3 | 0.45898 | 7.3 | 0.61197 | 7.3 | 0.76496 | 7.3 | 0.91796 | 7.3 | 1.071 | 7.3 | 1.2239 | 7.3 | 1.3769 | 7.3 | 1.5299
7.4 | 0.074405 | 7.4 | 0.14881 | 7.4 | 0.29762 | 7.4 | 0.44643 | 7.4 | 0.59524 | 7.4 | 0.74405 | 7.4 | 0.89286 | 7.4 | 1.0417 | 7.4 | 1.1905 | 7.4 | 1.3393 | 7.4 | 1.4881
7.5 | 0.072398 | 7.5 | 0.1448 | 7.5 | 0.28959 | 7.5 | 0.43439 | 7.5 | 0.57919 | 7.5 | 0.72398 | 7.5 | 0.86878 | 7.5 | 1.0136 | 7.5 | 1.1584 | 7.5 | 1.3032 | 7.5 | 1.448
7.6 | 0.070472 | 7.6 | 0.14094 | 7.6 | 0.28189 | 7.6 | 0.42283 | 7.6 | 0.56378 | 7.6 | 0.70472 | 7.6 | 0.84567 | 7.6 | 0.98661 | 7.6 | 1.1276 | 7.6 | 1.2685 | 7.6 | 1.4094
7.7 | 0.068622 | 7.7 | 0.13724 | 7.7 | 0.27449 | 7.7 | 0.41173 | 7.7 | 0.54898 | 7.7 | 0.68622 | 7.7 | 0.82347 | 7.7 | 0.96071 | 7.7 | 1.098 | 7.7 | 1.2352 | 7.7 | 1.3724
7.8 | 0.066845 | 7.8 | 0.13369 | 7.8 | 0.26738 | 7.8 | 0.40107 | 7.8 | 0.53476 | 7.8 | 0.66845 | 7.8 | 0.80214 | 7.8 | 0.93583 | 7.8 | 1.0695 | 7.8 | 1.2032 | 7.8 | 1.3369
7.9 | 0.065136 | 7.9 | 0.13027 | 7.9 | 0.26054 | 7.9 | 0.39082 | 7.9 | 0.52109 | 7.9 | 0.65136 | 7.9 | 0.78163 | 7.9 | 0.9119 | 7.9 | 1.0422 | 7.9 | 1.1724 | 7.9 | 1.3027
8 | 0.063492 | 8 | 0.12698 | 8 | 0.25397 | 8 | 0.38095 | 8 | 0.50794 | 8 | 0.63492 | 8 | 0.7619 | 8 | 0.88889 | 8 | 1.0159 | 8 | 1.1429 | 8 | 1.2698
8.1 | 0.06191 | 8.1 | 0.12382 | 8.1 | 0.24764 | 8.1 | 0.37146 | 8.1 | 0.49528 | 8.1 | 0.6191 | 8.1 | 0.74292 | 8.1 | 0.86674 | 8.1 | 0.99056 | 8.1 | 1.1144 | 8.1 | 1.2382
8.2 | 0.060386 | 8.2 | 0.12077 | 8.2 | 0.24155 | 8.2 | 0.36232 | 8.2 | 0.48309 | 8.2 | 0.60386 | 8.2 | 0.72464 | 8.2 | 0.84541 | 8.2 | 0.96618 | 8.2 | 1.087 | 8.2 | 1.2077
8.3 | 0.058919 | 8.3 | 0.11784 | 8.3 | 0.23568 | 8.3 | 0.35351 | 8.3 | 0.47135 | 8.3 | 0.58919 | 8.3 | 0.70703 | 8.3 | 0.82486 | 8.3 | 0.9427 | 8.3 | 1.0605 | 8.3 | 1.1784
8.4 | 0.057504 | 8.4 | 0.11501 | 8.4 | 0.23002 | 8.4 | 0.34503 | 8.4 | 0.46003 | 8.4 | 0.57504 | 8.4 | 0.69005 | 8.4 | 0.80506 | 8.4 | 0.92007 | 8.4 | 1.0351 | 8.4 | 1.1501
8.5 | 0.05614 | 8.5 | 0.11228 | 8.5 | 0.22456 | 8.5 | 0.33684 | 8.5 | 0.44912 | 8.5 | 0.5614 | 8.5 | 0.67368 | 8.5 | 0.78596 | 8.5 | 0.89825 | 8.5 | 1.0105 | 8.5 | 1.1228
8.6 | 0.054825 | 8.6 | 0.10965 | 8.6 | 0.2193 | 8.6 | 0.32895 | 8.6 | 0.4386 | 8.6 | 0.54825 | 8.6 | 0.65789 | 8.6 | 0.76754 | 8.6 | 0.87719 | 8.6 | 0.98684 | 8.6 | 1.0965
8.7 | 0.053555 | 8.7 | 0.10711 | 8.7 | 0.21422 | 8.7 | 0.32133 | 8.7 | 0.42844 | 8.7 | 0.53555 | 8.7 | 0.64266 | 8.7 | 0.74977 | 8.7 | 0.85688 | 8.7 | 0.96398 | 8.7 | 1.0711
8.8 | 0.052329 | 8.8 | 0.10466 | 8.8 | 0.20931 | 8.8 | 0.31397 | 8.8 | 0.41863 | 8.8 | 0.52329 | 8.8 | 0.62794 | 8.8 | 0.7326 | 8.8 | 0.83726 | 8.8 | 0.94192 | 8.8 | 1.0466
8.9 | 0.051144 | 8.9 | 0.10229 | 8.9 | 0.20458 | 8.9 | 0.30687 | 8.9 | 0.40915 | 8.9 | 0.51144 | 8.9 | 0.61373 | 8.9 | 0.71602 | 8.9 | 0.81831 | 8.9 | 0.9206 | 8.9 | 1.0229
9 | 0.05 | 9 | 0.1 | 9 | 0.2 | 9 | 0.3 | 9 | 0.4 | 9 | 0.5 | 9 | 0.6 | 9 | 0.7 | 9 | 0.8 | 9 | 0.9 | 9 | 1
9.1 | 0.048894 | 9.1 | 0.097788 | 9.1 | 0.19558 | 9.1 | 0.29336 | 9.1 | 0.39115 | 9.1 | 0.48894 | 9.1 | 0.58673 | 9.1 | 0.68451 | 9.1 | 0.7823 | 9.1 | 0.88009 | 9.1 | 0.97788
9.2 | 0.047824 | 9.2 | 0.095648 | 9.2 | 0.1913 | 9.2 | 0.28694 | 9.2 | 0.38259 | 9.2 | 0.47824 | 9.2 | 0.57389 | 9.2 | 0.66954 | 9.2 | 0.76518 | 9.2 | 0.86083 | 9.2 | 0.95648
9.3 | 0.046789 | 9.3 | 0.093578 | 9.3 | 0.18716 | 9.3 | 0.28073 | 9.3 | 0.37431 | 9.3 | 0.46789 | 9.3 | 0.56147 | 9.3 | 0.65505 | 9.3 | 0.74863 | 9.3 | 0.8422 | 9.3 | 0.93578
9.4 | 0.045788 | 9.4 | 0.091575 | 9.4 | 0.18315 | 9.4 | 0.27473 | 9.4 | 0.3663 | 9.4 | 0.45788 | 9.4 | 0.54945 | 9.4 | 0.64103 | 9.4 | 0.7326 | 9.4 | 0.82418 | 9.4 | 0.91575
9.5 | 0.044818 | 9.5 | 0.089636 | 9.5 | 0.17927 | 9.5 | 0.26891 | 9.5 | 0.35854 | 9.5 | 0.44818 | 9.5 | 0.53782 | 9.5 | 0.62745 | 9.5 | 0.71709 | 9.5 | 0.80672 | 9.5 | 0.89636
9.6 | 0.043879 | 9.6 | 0.087758 | 9.6 | 0.17552 | 9.6 | 0.26327 | 9.6 | 0.35103 | 9.6 | 0.43879 | 9.6 | 0.52655 | 9.6 | 0.6143 | 9.6 | 0.70206 | 9.6 | 0.78982 | 9.6 | 0.87758
9.7 | 0.042969 | 9.7 | 0.085938 | 9.7 | 0.17188 | 9.7 | 0.25782 | 9.7 | 0.34375 | 9.7 | 0.42969 | 9.7 | 0.51563 | 9.7 | 0.60157 | 9.7 | 0.68751 | 9.7 | 0.77345 | 9.7 | 0.85938
9.8 | 0.042088 | 9.8 | 0.084175 | 9.8 | 0.16835 | 9.8 | 0.25253 | 9.8 | 0.3367 | 9.8 | 0.42088 | 9.8 | 0.50505 | 9.8 | 0.58923 | 9.8 | 0.6734 | 9.8 | 0.75758 | 9.8 | 0.84175
9.9 | 0.041233 | 9.9 | 0.082466 | 9.9 | 0.16493 | 9.9 | 0.2474 | 9.9 | 0.32986 | 9.9 | 0.41233 | 9.9 | 0.49479 | 9.9 | 0.57726 | 9.9 | 0.65973 | 9.9 | 0.74219 | 9.9 | 0.82466
10 | 0.040404 | 10 | 0.080808 | 10 | 0.16162 | 10 | 0.24242 | 10 | 0.32323 | 10 | 0.40404 | 10 | 0.48485 | 10 | 0.56566 | 10 | 0.64646 | 10 | 0.72727 | 10 | 0.80808
10.5 | 0.036613 | 10.5 | 0.073227 | 10.5 | 0.14645 | 10.5 | 0.21968 | 10.5 | 0.29291 | 10.5 | 0.36613 | 10.5 | 0.43936 | 10.5 | 0.51259 | 10.5 | 0.58581 | 10.5 | 0.65904 | 10.5 | 0.73227
11 | 0.033333 | 11 | 0.066667 | 11 | 0.13333 | 11 | 0.2 | 11 | 0.26667 | 11 | 0.33333 | 11 | 0.4 | 11 | 0.46667 | 11 | 0.53333 | 11 | 0.6 | 11 | 0.66667
11.5 | 0.030476 | 11.5 | 0.060952 | 11.5 | 0.1219 | 11.5 | 0.18286 | 11.5 | 0.24381 | 11.5 | 0.30476 | 11.5 | 0.36571 | 11.5 | 0.42667 | 11.5 | 0.48762 | 11.5 | 0.54857 | 11.5 | 0.60952
12 | 0.027972 | 12 | 0.055944 | 12 | 0.11189 | 12 | 0.16783 | 12 | 0.22378 | 12 | 0.27972 | 12 | 0.33566 | 12 | 0.39161 | 12 | 0.44755 | 12 | 0.5035 | 12 | 0.55944
12.5 | 0.025765 | 12.5 | 0.05153 | 12.5 | 0.10306 | 12.5 | 0.15459 | 12.5 | 0.20612 | 12.5 | 0.25765 | 12.5 | 0.30918 | 12.5 | 0.36071 | 12.5 | 0.41224 | 12.5 | 0.46377 | 12.5 | 0.5153
13 | 0.02381 | 13 | 0.047619 | 13 | 0.095238 | 13 | 0.14286 | 13 | 0.19048 | 13 | 0.2381 | 13 | 0.28571 | 13 | 0.33333 | 13 | 0.38095 | 13 | 0.42857 | 13 | 0.47619
13.5 | 0.022069 | 13.5 | 0.044138 | 13.5 | 0.088276 | 13.5 | 0.13241 | 13.5 | 0.17655 | 13.5 | 0.22069 | 13.5 | 0.26483 | 13.5 | 0.30897 | 13.5 | 0.3531 | 13.5 | 0.39724 | 13.5 | 0.44138
14 | 0.020513 | 14 | 0.041026 | 14 | 0.082051 | 14 | 0.12308 | 14 | 0.1641 | 14 | 0.20513 | 14 | 0.24615 | 14 | 0.28718 | 14 | 0.32821 | 14 | 0.36923 | 14 | 0.41026
14.5 | 0.019116 | 14.5 | 0.038232 | 14.5 | 0.076464 | 14.5 | 0.1147 | 14.5 | 0.15293 | 14.5 | 0.19116 | 14.5 | 0.22939 | 14.5 | 0.26762 | 14.5 | 0.30585 | 14.5 | 0.34409 | 14.5 | 0.38232
15 | 0.017857 | 15 | 0.035714 | 15 | 0.071429 | 15 | 0.10714 | 15 | 0.14286 | 15 | 0.17857 | 15 | 0.21429 | 15 | 0.25 | 15 | 0.28571 | 15 | 0.32143 | 15 | 0.35714
16 | 0.015686 | 16 | 0.031373 | 16 | 0.062745 | 16 | 0.094118 | 16 | 0.12549 | 16 | 0.15686 | 16 | 0.18824 | 16 | 0.21961 | 16 | 0.25098 | 16 | 0.28235 | 16 | 0.31373
17 | 0.013889 | 17 | 0.027778 | 17 | 0.055556 | 17 | 0.083333 | 17 | 0.11111 | 17 | 0.13889 | 17 | 0.16667 | 17 | 0.19444 | 17 | 0.22222 | 17 | 0.25 | 17 | 0.27778
18 | 0.012384 | 18 | 0.024768 | 18 | 0.049536 | 18 | 0.074303 | 18 | 0.099071 | 18 | 0.12384 | 18 | 0.14861 | 18 | 0.17337 | 18 | 0.19814 | 18 | 0.22291 | 18 | 0.24768
19 | 0.011111 | 19 | 0.022222 | 19 | 0.044444 | 19 | 0.066667 | 19 | 0.088889 | 19 | 0.11111 | 19 | 0.13333 | 19 | 0.15556 | 19 | 0.17778 | 19 | 0.2 | 19 | 0.22222
20 | 0.010025 | 20 | 0.02005 | 20 | 0.0401 | 20 | 0.06015 | 20 | 0.080201 | 20 | 0.10025 | 20 | 0.1203 | 20 | 0.14035 | 20 | 0.1604 | 20 | 0.18045 | 20 | 0.2005
|  | 21 | 0.018182 | 21 | 0.036364 | 21 | 0.054545 | 21 | 0.072727 | 21 | 0.090909 | 21 | 0.10909 | 21 | 0.12727 | 21 | 0.14545 | 21 | 0.16364 | 21 | 0.18182
|  | 22 | 0.016563 | 22 | 0.033126 | 22 | 0.049689 | 22 | 0.066253 | 22 | 0.082816 | 22 | 0.099379 | 22 | 0.11594 | 22 | 0.13251 | 22 | 0.14907 | 22 | 0.16563
|  | 23 | 0.015152 | 23 | 0.030303 | 23 | 0.045455 | 23 | 0.060606 | 23 | 0.075758 | 23 | 0.090909 | 23 | 0.10606 | 23 | 0.12121 | 23 | 0.13636 | 23 | 0.15152
|  | 24 | 0.013913 | 24 | 0.027826 | 24 | 0.041739 | 24 | 0.055652 | 24 | 0.069565 | 24 | 0.083478 | 24 | 0.097391 | 24 | 0.1113 | 24 | 0.12522 | 24 | 0.13913
|  | 25 | 0.012821 | 25 | 0.025641 | 25 | 0.038462 | 25 | 0.051282 | 25 | 0.064103 | 25 | 0.076923 | 25 | 0.089744 | 25 | 0.10256 | 25 | 0.11538 | 25 | 0.12821
|  | 26 | 0.011852 | 26 | 0.023704 | 26 | 0.035556 | 26 | 0.047407 | 26 | 0.059259 | 26 | 0.071111 | 26 | 0.082963 | 26 | 0.094815 | 26 | 0.10667 | 26 | 0.11852
|  | 27 | 0.010989 | 27 | 0.021978 | 27 | 0.032967 | 27 | 0.043956 | 27 | 0.054945 | 27 | 0.065934 | 27 | 0.076923 | 27 | 0.087912 | 27 | 0.098901 | 27 | 0.10989
|  | 28 | 0.010217 | 28 | 0.020434 | 28 | 0.030651 | 28 | 0.040868 | 28 | 0.051086 | 28 | 0.061303 | 28 | 0.07152 | 28 | 0.081737 | 28 | 0.091954 | 28 | 0.10217
|  | 29 | 0.0095238 | 29 | 0.019048 | 29 | 0.028571 | 29 | 0.038095 | 29 | 0.047619 | 29 | 0.057143 | 29 | 0.066667 | 29 | 0.07619 | 29 | 0.085714 | 29 | 0.095238
|  |  |  | 30 | 0.017798 | 30 | 0.026696 | 30 | 0.035595 | 30 | 0.044494 | 30 | 0.053393 | 30 | 0.062291 | 30 | 0.07119 | 30 | 0.080089 | 30 | 0.088988
|  |  |  | 31 | 0.017798 | 31 | 0.026696 | 31 | 0.035595 | 31 | 0.044494 | 31 | 0.053393 | 31 | 0.062291 | 31 | 0.07119 | 31 | 0.080089 | 31 | 0.088988
|  |  |  | 32 | 0.017798 | 32 | 0.026696 | 32 | 0.035595 | 32 | 0.044494 | 32 | 0.053393 | 32 | 0.062291 | 32 | 0.07119 | 32 | 0.080089 | 32 | 0.088988
|  |  |  | 33 | 0.017798 | 33 | 0.026696 | 33 | 0.035595 | 33 | 0.044494 | 33 | 0.053393 | 33 | 0.062291 | 33 | 0.07119 | 33 | 0.080089 | 33 | 0.088988
|  |  |  | 34 | 0.017798 | 34 | 0.026696 | 34 | 0.035595 | 34 | 0.044494 | 34 | 0.053393 | 34 | 0.062291 | 34 | 0.07119 | 34 | 0.080089 | 34 | 0.088988
|  |  |  | 35 | 0.017798 | 35 | 0.026696 | 35 | 0.035595 | 35 | 0.044494 | 35 | 0.053393 | 35 | 0.062291 | 35 | 0.07119 | 35 | 0.080089 | 35 | 0.088988
|  |  |  | 36 | 0.017798 | 36 | 0.026696 | 36 | 0.035595 | 36 | 0.044494 | 36 | 0.053393 | 36 | 0.062291 | 36 | 0.07119 | 36 | 0.080089 | 36 | 0.088988
|  |  |  | 37 | 0.017798 | 37 | 0.026696 | 37 | 0.035595 | 37 | 0.044494 | 37 | 0.053393 | 37 | 0.062291 | 37 | 0.07119 | 37 | 0.080089 | 37 | 0.088988
|  |  |  | 38 | 0.017798 | 38 | 0.026696 | 38 | 0.035595 | 38 | 0.044494 | 38 | 0.053393 | 38 | 0.062291 | 38 | 0.07119 | 38 | 0.080089 | 38 | 0.088988
|  |  |  | 39 | 0.017798 | 39 | 0.026696 | 39 | 0.035595 | 39 | 0.044494 | 39 | 0.053393 | 39 | 0.062291 | 39 | 0.07119 | 39 | 0.080089 | 39 | 0.088988
|  |  |  | 40 | 0.017798 | 40 | 0.026696 | 40 | 0.035595 | 40 | 0.044494 | 40 | 0.053393 | 40 | 0.062291 | 40 | 0.07119 | 40 | 0.080089 | 40 | 0.088988
|  |  |  | 41 | 0.017798 | 41 | 0.026696 | 41 | 0.035595 | 41 | 0.044494 | 41 | 0.053393 | 41 | 0.062291 | 41 | 0.07119 | 41 | 0.080089 | 41 | 0.088988
|  |  |  | 42 | 0.017798 | 42 | 0.026696 | 42 | 0.035595 | 42 | 0.044494 | 42 | 0.053393 | 42 | 0.062291 | 42 | 0.07119 | 42 | 0.080089 | 42 | 0.088988
|  |  |  | 43 | 0.017798 | 43 | 0.026696 | 43 | 0.035595 | 43 | 0.044494 | 43 | 0.053393 | 43 | 0.062291 | 43 | 0.07119 | 43 | 0.080089 | 43 | 0.088988
|  |  |  | 44 | 0.017798 | 44 | 0.026696 | 44 | 0.035595 | 44 | 0.044494 | 44 | 0.053393 | 44 | 0.062291 | 44 | 0.07119 | 44 | 0.080089 | 44 | 0.088988
|  |  |  | 45 | 0.017798 | 45 | 0.026696 | 45 | 0.035595 | 45 | 0.044494 | 45 | 0.053393 | 45 | 0.062291 | 45 | 0.07119 | 45 | 0.080089 | 45 | 0.088988
|  |  |  | 46 | 0.017798 | 46 | 0.026696 | 46 | 0.035595 | 46 | 0.044494 | 46 | 0.053393 | 46 | 0.062291 | 46 | 0.07119 | 46 | 0.080089 | 46 | 0.088988
|  |  |  | 47 | 0.017798 | 47 | 0.026696 | 47 | 0.035595 | 47 | 0.044494 | 47 | 0.053393 | 47 | 0.062291 | 47 | 0.07119 | 47 | 0.080089 | 47 | 0.088988
|  |  |  | 48 | 0.017798 | 48 | 0.026696 | 48 | 0.035595 | 48 | 0.044494 | 48 | 0.053393 | 48 | 0.062291 | 48 | 0.07119 | 48 | 0.080089 | 48 | 0.088988
|  |  |  | 49 | 0.017798 | 49 | 0.026696 | 49 | 0.035595 | 49 | 0.044494 | 49 | 0.053393 | 49 | 0.062291 | 49 | 0.07119 | 49 | 0.080089 | 49 | 0.088988
|  |  |  | 50 | 0.017798 | 50 | 0.026696 | 50 | 0.035595 | 50 | 0.044494 | 50 | 0.053393 | 50 | 0.062291 | 50 | 0.07119 | 50 | 0.080089 | 50 | 0.088988
|  |  |  | 55 | 0.017798 | 55 | 0.026696 | 55 | 0.035595 | 55 | 0.044494 | 55 | 0.053393 | 55 | 0.062291 | 55 | 0.07119 | 55 | 0.080089 | 55 | 0.088988
|  |  |  | 60 | 0.017798 | 60 | 0.026696 | 60 | 0.035595 | 60 | 0.044494 | 60 | 0.053393 | 60 | 0.062291 | 60 | 0.07119 | 60 | 0.080089 | 60 | 0.088988
|  |  |  | 65 | 0.017798 | 65 | 0.026696 | 65 | 0.035595 | 65 | 0.044494 | 65 | 0.053393 | 65 | 0.062291 | 65 | 0.07119 | 65 | 0.080089 | 65 | 0.088988
|  |  |  | 70 | 0.017798 | 70 | 0.026696 | 70 | 0.035595 | 70 | 0.044494 | 70 | 0.053393 | 70 | 0.062291 | 70 | 0.07119 | 70 | 0.080089 | 70 | 0.088988
|  |  |  | 75 | 0.017798 | 75 | 0.026696 | 75 | 0.035595 | 75 | 0.044494 | 75 | 0.053393 | 75 | 0.062291 | 75 | 0.07119 | 75 | 0.080089 | 75 | 0.088988
|  |  |  | 80 | 0.017798 | 80 | 0.026696 | 80 | 0.035595 | 80 | 0.044494 | 80 | 0.053393 | 80 | 0.062291 | 80 | 0.07119 | 80 | 0.080089 | 80 | 0.088988
|  |  |  | 85 | 0.017798 | 85 | 0.026696 | 85 | 0.035595 | 85 | 0.044494 | 85 | 0.053393 | 85 | 0.062291 | 85 | 0.07119 | 85 | 0.080089 | 85 | 0.088988
|  |  |  | 90 | 0.017798 | 90 | 0.026696 | 90 | 0.035595 | 90 | 0.044494 | 90 | 0.053393 | 90 | 0.062291 | 90 | 0.07119 | 90 | 0.080089 | 90 | 0.088988
|  |  |  | 95 | 0.017798 | 95 | 0.026696 | 95 | 0.035595 | 95 | 0.044494 | 95 | 0.053393 | 95 | 0.062291 | 95 | 0.07119 | 95 | 0.080089 | 95 | 0.088988
|  |  |  | 100 | 0.017798 | 100 | 0.026696 | 100 | 0.035595 | 100 | 0.044494 | 100 | 0.053393 | 100 | 0.062291 | 100 | 0.07119 | 100 | 0.080089 | 100 | 0.088988