## KSR Total Clear
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal and Extra-Performance Styles | [9 empty] | Universal and Extra-Performance Styles | [9 empty] | Universal and Extra-Performance Styles | [9 empty] | Universal and Extra-Performance Styles
"KSR" Speed (TCC 171-6-2) | [9 empty] | "KSR" Speed (TCC 171-6-2) | [9 empty] | "KSR" Speed (TCC 171-6-2) | [9 empty] | "KSR" Speed (TCC 171-6-2)
Total Clearing Time-Current Characteristic Curves Dated September 27, 2004 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated September 27, 2004 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated September 27, 2004 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated September 27, 2004
Tolerance: | Curves are plotted to maximum test points. All variations are minus. | [8 empty] | Tolerance: | Curves are plotted to maximum test points. All variations are minus. | [8 empty] | Tolerance: | Curves are plotted to maximum test points. All variations are minus. | [8 empty] | Tolerance: | Curves are plotted to maximum test points. All variations are minus.
3 KSR |  | 5 KSR |  | 7 KSR |  | 10 KSR |  | 15 KSR |  | 20 KSR |  | 25 KSR |  | 30 KSR |  | 40 KSR |  | 50 KSR |  | 65 KSR |  | 80 KSR |  | 100 KSR |  | 125 KSR |  | 150 KSR |  | 200 KSR
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
10000 | 0.0133 | 10000 | 0.0133 | 10000 | 0.0133 | 10000 | 0.0133 | 10000 | 0.0133 | 10000 | 0.0133 | 10000 | 0.0133 | 10000 | 0.014 | 10000 | 0.01515 | 10000 | 0.017 | 10000 | 0.02 | 10000 | 0.0245 | 10000 | 0.033 | 10000 | 0.04 | 10000 | 0.055 | 10000 | 0.122
2000 | 0.0133 | 3000 | 0.0133 | 3500 | 0.0133 | 6000 | 0.0133 | 8000 | 0.01331 | 9000 | 0.013325 | 9000 | 0.0135 | 9000 | 0.0144 | 9000 | 0.016 | 9000 | 0.0181 | 9000 | 0.02225 | 9000 | 0.0271 | 9000 | 0.0368 | 9000 | 0.0455 | 9000 | 0.0635 | 9000 | 0.1435
1900 | 0.01331 | 2500 | 0.01334 | 3300 | 0.01333 | 5000 | 0.0134 | 7500 | 0.01332 | 8000 | 0.01335 | 8000 | 0.013825 | 8000 | 0.015 | 8000 | 0.0171 | 8000 | 0.0197 | 8000 | 0.025 | 8000 | 0.031 | 8000 | 0.0421 | 8000 | 0.054 | 8000 | 0.0775 | 8000 | 0.173
1700 | 0.0134 | 2300 | 0.01351 | 3000 | 0.0134 | 4500 | 0.0135 | 7000 | 0.01335 | 7000 | 0.0135 | 7000 | 0.01425 | 7000 | 0.016 | 7400 | 0.018 | 7000 | 0.0215 | 7000 | 0.0292 | 7000 | 0.036 | 7000 | 0.05 | 7000 | 0.066 | 7000 | 0.095 | 7000 | 0.222
1500 | 0.01355 | 2100 | 0.01361 | 2500 | 0.01395 | 4000 | 0.0138 | 6000 | 0.0136 | 6600 | 0.0136 | 6400 | 0.0148 | 6000 | 0.0173 | 7000 | 0.01865 | 6400 | 0.0232 | 6000 | 0.0346 | 6000 | 0.043 | 6600 | 0.0548 | 6000 | 0.084 | 6000 | 0.123 | 6000 | 0.29
1300 | 0.0138 | 2000 | 0.0137 | 2200 | 0.0146 | 3500 | 0.0142 | 5600 | 0.0138 | 6000 | 0.01381 | 6000 | 0.01515 | 5000 | 0.01985 | 6400 | 0.01985 | 6000 | 0.0245 | 5000 | 0.0434 | 5000 | 0.0556 | 6000 | 0.063 | 5600 | 0.094 | 5000 | 0.176 | 5000 | 0.434
1200 | 0.01395 | 1900 | 0.01382 | 2000 | 0.015 | 3000 | 0.015 | 5000 | 0.0142 | 5400 | 0.01425 | 5400 | 0.01595 | 4500 | 0.0217 | 6000 | 0.0208 | 5600 | 0.0263 | 4500 | 0.049 | 4500 | 0.065 | 5400 | 0.074 | 5000 | 0.1165 | 4000 | 0.275 | 4816.0999 | 0.4878
1000 | 0.01455 | 1700 | 0.014 | 1900 | 0.01545 | 2500 | 0.0168 | 4700 | 0.0144 | 5000 | 0.01464 | 5000 | 0.01645 | 4000 | 0.02385 | 5600 | 0.0219 | 5000 | 0.02965 | 4000 | 0.058 | 4000 | 0.078 | 5000 | 0.085 | 4500 | 0.1385 | 3520.4282 | 0.34955 | 4297.2982 | 0.61518
900 | 0.0151 | 1500 | 0.01445 | 1700 | 0.0164 | 2200 | 0.018 | 4500 | 0.01455 | 4500 | 0.0152 | 4700 | 0.01715 | 3500 | 0.027 | 5000 | 0.0243 | 4500 | 0.033 | 3700 | 0.065 | 3800 | 0.0843 | 4500 | 0.103 | 4000 | 0.176 | 3113.8342 | 0.45183 | 3780.9026 | 0.7656
800 | 0.0159 | 1300 | 0.01515 | 1500 | 0.01762 | 2000 | 0.0192 | 4200 | 0.01495 | 4000 | 0.0161 | 4500 | 0.01755 | 3000 | 0.03175 | 4600 | 0.0262 | 4000 | 0.038 | 3500 | 0.071 | 3500 | 0.096 | 4000 | 0.128 | 3500 | 0.233 | 2749.7644 | 0.58891 | 3367.4061 | 0.91997
700 | 0.01725 | 1200 | 0.01565 | 1400 | 0.0184 | 1900 | 0.0199 | 4000 | 0.0152 | 3700 | 0.01677 | 4200 | 0.0182 | 2800 | 0.0343 | 4300 | 0.02785 | 3600 | 0.0433 | 3300 | 0.077 | 3300 | 0.1065 | 3500 | 0.161 | 3221.7771 | 0.2755 | 2436.1021 | 0.75652 | 3055.5929 | 1.0767
600 | 0.01875 | 1100 | 0.0163 | 1200 | 0.0202 | 1700 | 0.02175 | 3700 | 0.01585 | 3500 | 0.0174 | 4000 | 0.019 | 2600 | 0.0374 | 4000 | 0.03 | 3300 | 0.0485 | 3000 | 0.089 | 3000 | 0.126 | 3000 | 0.217 | 2835.277 | 0.36132 | 2089.7556 | 0.97385 | 2712.0362 | 1.2985
500 | 0.02125 | 1000 | 0.01725 | 1100 | 0.0217 | 1500 | 0.0241 | 3500 | 0.01615 | 3300 | 0.018 | 3800 | 0.0196 | 2400 | 0.0416 | 3600 | 0.0339 | 3000 | 0.0557 | 2800 | 0.1 | 2800 | 0.1415 | 2500 | 0.316 | 2568.5942 | 0.44672 | 1795.5417 | 1.2575 | 2452.9884 | 1.5245
450 | 0.023 | 900 | 0.0183 | 1000 | 0.0234 | 1400 | 0.02538 | 3200 | 0.017 | 3000 | 0.01925 | 3600 | 0.0204 | 2200 | 0.047 | 3300 | 0.03755 | 2800 | 0.062 | 2500 | 0.1215 | 2500 | 0.175 | 2476.2557 | 0.31945 | 2382.8433 | 0.52391 | 1543.105 | 1.6154 | 2158.7159 | 1.8557
400 | 0.0252 | 800 | 0.0199 | 900 | 0.0257 | 1200 | 0.03 | 3000 | 0.01765 | 2800 | 0.02045 | 3400 | 0.0213 | 2000 | 0.053 | 3000 | 0.0427 | 2600 | 0.0692 | 2300 | 0.1415 | 2000 | 0.276 | 2193.7922 | 0.4217 | 2233.549 | 0.60534 | 1294.7785 | 2.1528 | 1909.3937 | 2.2896
350 | 0.029 | 700 | 0.02215 | 800 | 0.0288 | 1100 | 0.033 | 2800 | 0.01835 | 2600 | 0.0215 | 3200 | 0.0224 | 1700 | 0.068 | 2800 | 0.0465 | 2400 | 0.078 | 2000 | 0.1875 | 1500 | 0.51 | 2014.6309 | 0.51286 | 2054.4496 | 0.74473 | 1135.5218 | 2.7479 | 1660.3341 | 2.9966
300 | 0.034 | 600 | 0.025 | 760 | 0.0306 | 1000 | 0.037 | 2600 | 0.01915 | 2400 | 0.0231 | 3000 | 0.02385 | 1500 | 0.084 | 2600 | 0.0511 | 2200 | 0.091 | 1846.2712 | 0.21737 | 1461.1523 | 0.52845 | 1896.6862 | 0.59 | 1928.8368 | 0.8531 | 1103.0507 | 2.899 | 1511.804 | 3.6365
260 | 0.0404 | 500 | 0.03 | 700 | 0.0338 | 900 | 0.0424 | 2200 | 0.0215 | 2200 | 0.025 | 2800 | 0.02515 | 1400 | 0.095 | 2400 | 0.0575 | 2000 | 0.1085 | 1583.4177 | 0.29929 | 1319.4578 | 0.67233 | 1781.9499 | 0.68355 | 1762.3635 | 1 | 955.8626 | 3.7941 | 1367.0849 | 4.4681
240 | 0.045 | 450 | 0.0335 | 660 | 0.03615 | 800 | 0.0491 | 2000 | 0.0233 | 2000 | 0.02725 | 2600 | 0.0272 | 1300 | 0.1075 | 2200 | 0.0655 | 1858.213 | 0.12201 | 1429.8665 | 0.36926 | 1184.6648 | 0.86458 | 1623.78 | 0.82224 | 1618.4358 | 1.1528 | 818.6448 | 5.2185 | 1226.0142 | 5.669
220 | 0.05085 | 400 | 0.0383 | 600 | 0.0408 | 760 | 0.0526 | 1900 | 0.0245 | 1900 | 0.02875 | 2400 | 0.0293 | 1200 | 0.1245 | 2000 | 0.076 | 1524.0369 | 0.1782 | 1298.0622 | 0.45183 | 1138.4016 | 0.95 | 1519.02 | 0.91833 | 1498.9788 | 1.3 | 735.3524 | 6.7177 | 1119.9419 | 6.8653
200 | 0.058 | 370 | 0.0427 | 560 | 0.0445 | 700 | 0.06 | 1700 | 0.0272 | 1700 | 0.03225 | 2200 | 0.0324 | 1100 | 0.1485 | 1900 | 0.083 | 1265.8886 | 0.25705 | 1193.7008 | 0.54889 | 1089.504 | 1.05 | 1420.3504 | 1.0203 | 1371.8148 | 1.4994 | 672.9697 | 8.3399 | 1014.6015 | 8.6386
160 | 0.082 | 350 | 0.0456 | 500 | 0.0525 | 660 | 0.066 | 1500 | 0.0315 | 1500 | 0.0371 | 2000 | 0.036 | 1000 | 0.178 | 1800 | 0.0925 | 1109.1633 | 0.33992 | 1111.9762 | 0.64975 | 1020.2239 | 1.1684 | 1319.4578 | 1.15 | 1251.3981 | 1.75 | 593.1923 | 11.5663 | 912.8417 | 11.2592
140 | 0.1065 | 320 | 0.0515 | 450 | 0.0611 | 600 | 0.0776 | 1300 | 0.0374 | 1400 | 0.0408 | 1900 | 0.0384 | 920.864 | 0.20137 | 1700 | 0.103 | 988.5428 | 0.44075 | 1024.6971 | 0.80749 | 838.0993 | 1.5971 | 1230.256 | 1.2945 | 1155.0359 | 1.9808 | 539.106 | 15.7036 | 850.7279 | 13.7913
120 | 0.1425 | 300 | 0.056 | 400 | 0.074 | 560 | 0.088 | 1100 | 0.047 | 1300 | 0.04475 | 1700 | 0.044 | 832.1383 | 0.24842 | 1500 | 0.135 | 923.1993 | 0.51523 | 881.0397 | 1.1061 | 712.3534 | 2.0903 | 1152.36 | 1.4555 | 1068.552 | 2.25 | 508.5674 | 19.7709 | 798.3272 | 17.2641
100 | 0.2015 | 270 | 0.066 | 350 | 0.093 | 500 | 0.109 | 1000 | 0.0535 | 1200 | 0.05 | 1500 | 0.052 | 748.5064 | 0.30841 | 990.1375 | 0.30266 | 853.2877 | 0.61954 | 755.2583 | 1.4135 | 611.2171 | 2.7329 | 1094.1969 | 1.574 | 1002.5256 | 2.5393 | 478.2095 | 26.3633 | 747.7748 | 22.5014
88.9601 | 0.2523 | 250 | 0.075 | 300 | 0.127 | 450 | 0.133 | 960 | 0.0565 | 1100 | 0.0574 | 1400 | 0.058 | 688.9624 | 0.36308 | 914.5248 | 0.35624 | 770.1858 | 0.79983 | 664.0419 | 1.7603 | 537.5211 | 3.4531 | 1028.0056 | 1.7498 | 946.2273 | 2.8054 | 457.3871 | 34.4308 | 711.1419 | 28.3429
78.5589 | 0.31846 | 220 | 0.0935 | 250 | 0.1825 | 400 | 0.1698 | 900 | 0.062 | 1000 | 0.0675 | 1300 | 0.0645 | 621.1486 | 0.45043 | 861.1831 | 0.40179 | 723.9282 | 0.95 | 578.6227 | 2.2127 | 480.7237 | 4.336 | 881.4456 | 2.3281 | 889.8063 | 3.1297 | 440.398 | 44.8295 | 674.1212 | 36.2219
64.0023 | 0.48306 | 200 | 0.11 | 200 | 0.29 | 350 | 0.2235 | 860 | 0.067 | 900 | 0.078 | 1200 | 0.0725 | 571.7359 | 0.53703 | 816.01 | 0.45106 | 680.6056 | 1.1106 | 515.3419 | 2.7386 | 434.1057 | 5.5081 | 757.1736 | 3.1103 | 825.6491 | 3.6 | 424.1334 | 56.8191 | 643.3051 | 44.6905
59.593 | 0.56095 | 150 | 0.19445 | 182.8923 | 0.33963 | 334.3455 | 0.24207 | 800 | 0.0745 | 800 | 0.098 | 1100 | 0.085 | 536.0379 | 0.62858 | 776.7754 | 0.50653 | 628.56 | 1.3 | 454.8786 | 3.4854 | 377.4813 | 7.6852 | 685.9548 | 3.7931 | 771.2506 | 4.1173 | 407.7134 | 73.8266 | 602.5495 | 58.5503
52.7467 | 0.7372 | 140.0217 | 0.2173 | 155.6666 | 0.46802 | 302.1311 | 0.30061 | 700 | 0.095 | 700 | 0.1275 | 1000 | 0.102 | 484.3904 | 0.78119 | 740.7906 | 0.56205 | 582.4994 | 1.4791 | 400.217 | 4.5616 | 334.4225 | 10.3538 | 617.0147 | 4.8306 | 719.1103 | 4.7863 | 391.9257 | 97.6274 | 572.0908 | 73.5977
46.3656 | 1 | 121.3935 | 0.28379 | 133.7197 | 0.64107 | 254.2117 | 0.42949 | 600 | 0.1235 | 346.0951 | 0.502 | 900 | 0.1225 | 434.7059 | 1.0161 | 708.2645 | 0.63245 | 554.62 | 1.62 | 353.8307 | 5.8842 | 301.8482 | 14.0944 | 560.2676 | 6.1944 | 682.1745 | 5.411 | 378.659 | 123.5947 | 546.9334 | 93.7653
41.5141 | 1.3026 | 100.045 | 0.41638 | 115.9299 | 0.85656 | 223.4578 | 0.56444 | 560.0096 | 0.1406 | 319.2975 | 0.59383 | 869.3517 | 0.12929 | 394.6349 | 1.3039 | 675.4536 | 0.70811 | 509.3256 | 1.8596 | 319.1505 | 7.4989 | 280.3349 | 18.5037 | 513.6834 | 7.7983 | 641.4983 | 6.25 | 368.3738 | 154.575 | 520.2364 | 120.2264
36.8295 | 1.735 | 78.3782 | 0.69984 | 101.4368 | 1.1552 | 190.6319 | 0.77475 | 488.8724 | 0.18382 | 297.3004 | 0.69896 | 767.707 | 0.16421 | 359.9113 | 1.6071 | 640.1703 | 0.79999 | 438.6271 | 2.4591 | 288.4666 | 9.6903 | 263.245 | 24.0922 | 469.0245 | 10.0581 | 610.6544 | 7.0016 | 358.2817 | 190.517 | 503.2251 | 150.783
32.9 | 2.3351 | 68.3275 | 0.92574 | 86.1381 | 1.6305 | 166.0334 | 1.0298 | 430.7204 | 0.2381 | 278.7376 | 0.81127 | 684.2196 | 0.20598 | 314.9166 | 2.0097 | 602.8309 | 0.9147 | 394.2716 | 3.0269 | 268.1117 | 12.1806 | 248.6784 | 31.3685 | 428.0316 | 13.2595 | 579.1559 | 8 | 350.3135 | 233.605 | 487.6672 | 191.11
30.3526 | 2.884 | 58.5727 | 1.3045 | 76.9477 | 2.086 | 146.2835 | 1.352 | 380.3606 | 0.31194 | 256.5639 | 1.0008 | 610.6544 | 0.25892 | 278.7376 | 2.4616 | 568.847 | 1.0691 | 340.3263 | 4.0738 | 250.054 | 15.5828 | 234.429 | 41.783 | 397.8803 | 16.9104 | 552.1988 | 8.9944 | 341.4168 | 300 | 476.6291 | 230.483
27.938 | 3.6515 | 51.784 | 1.7055 | 70.6636 | 2.5235 | 131.885 | 1.7189 | 339.7782 | 0.39537 | 229.7182 | 1.298 | 536.4083 | 0.33433 | 238.3392 | 3.2184 | 559.108 | 1.1318 | 297.2319 | 5.5014 | 229.5347 | 21.4775 | 224.3258 | 53.6196 | 374.3909 | 21.0811 | 531.8577 | 10 |  |  | 464.3378 | 278.832
26.609 | 4.2073 | 46.1525 | 2.2075 | 64.8926 | 3.1265 | 121.6734 | 2.0688 | 304.9267 | 0.50119 | 215.8716 | 1.4991 | 483.2763 | 0.41852 | 209.5055 | 4.1387 | 429.81 | 1.8019 | 261.2736 | 7.4811 | 218.5547 | 26.7746 | 214.3099 | 71.4215 | 350.747 | 27.2217 | 514.1746 | 11.2826 |  |  | 460.7708 | 300
25.6033 | 4.7889 | 42.4811 | 2.7178 | 60.0061 | 3.7902 | 114.3656 | 2.3864 | 273.65 | 0.62806 | 194.6236 | 2.0154 | 438.7281 | 0.51477 | 183.7365 | 5.4054 | 331.737 | 2.912 | 235.8281 | 9.6502 | 206.7612 | 34.1469 | 205.8736 | 96.7223 | 333.0116 | 34.914 | 494.2219 | 13
25.2 | 5.2 | 39.5545 | 3.2215 | 56.5191 | 4.5193 | 106.6094 | 2.8396 | 243.8908 | 0.8 | 179.9681 | 2.5366 | 407.5637 | 0.60937 | 160.3967 | 7.2599 | 266.225 | 4.5306 | 216.3088 | 12.3712 | 196.8682 | 43.6844 | 197.4031 | 137.942 | 315.5885 | 46.1476 | 480.4372 | 14.3219
24.8 | 5.7148 | 37.6007 | 3.6559 | 53.4805 | 5.3442 | 97.9931 | 3.5071 | 212.42 | 1.089 | 169.5101 | 2.9444 | 369.1437 | 0.75184 | 139.6997 | 10.0373 | 221.926 | 6.7184 | 197.1281 | 16.771 | 187.8792 | 55.0251 | 191.0743 | 182.791 | 300.7317 | 59.282 | 456.6118 | 17
24.4 | 6.3 | 35.0103 | 4.4143 | 48.5507 | 6.8865 | 89.3708 | 4.354 | 195.9 | 1.3188 | 154.595 | 3.55 | 338.9967 | 0.92378 | 124.649 | 13.8056 | 196.045 | 8.8893 | 181.225 | 22.5944 | 180.0857 | 69.8137 | 184.8614 | 262.315 | 288.6249 | 74.2864 | 440.6118 | 19.3658
24.05 | 6.9655 | 33.128 | 5.0523 | 43.6712 | 8.2711 | 82.0721 | 5.2947 | 164.407 | 2.0398 | 143.2833 | 4.15 | 302.8276 | 1.1892 | 113.2862 | 18.6962 | 180.61 | 10.89 | 168.3387 | 29.8791 | 172.8928 | 88.1049 | 184.2404 | 300 | 275.1595 | 95.8255 | 426.6421 | 22
23.8853 | 7.5 | 31.7099 | 5.6851 | 38.2116 | 10.4183 | 72.3095 | 6.7038 | 149.059 | 2.4469 | 136.5198 | 4.4676 | 276.1821 | 1.5229 | 105.3562 | 24.0175 | 167.058 | 13.5426 | 158.0685 | 39.4301 | 167.9857 | 108.1434 |  |  | 265.2356 | 120.203 | 418.7643 | 24.2423
23.5 | 8.2794 | 30.75 | 6.3525 | 33.688 | 13.1774 | 62.6896 | 8.4006 | 134.739 | 2.9887 | 129.1801 | 4.9821 | 253.627 | 1.9143 | 96.8586 | 32.9662 | 156.858 | 16.7575 | 146.8596 | 54.6279 | 162.9163 | 134.976 |  |  | 256.4928 | 152.983 | 405.4844 | 28.2488
22.5525 | 9.2257 | 30.0051 | 6.8131 | 31.0994 | 16.0576 | 55.7437 | 10.4075 | 123.76 | 3.5746 | 118.6303 | 5.9646 | 234.5284 | 2.2439 | 90.9099 | 45.2959 | 148.91 | 20.5291 | 140.8494 | 67.3998 | 158.509 | 167.224 |  |  | 249.6406 | 192.699 | 398.7288 | 31.3036
19.9246 | 11.4815 | 28.9865 | 7.7978 | 27.9271 | 21.4553 | 48.3698 | 13.706 | 110.095 | 4.4989 | 109.4449 | 6.9507 | 220.3918 | 2.4693 | 86.712 | 60.7101 | 139.958 | 26.7049 | 133.9688 | 86.4968 | 155.1103 | 202.723 |  |  | 241.297 | 256.41 | 391.3625 | 35.2371
18.0128 | 13.7202 | 28.392 | 8.6525 | 25.509 | 27.5904 | 42.9485 | 17.8639 | 98.1352 | 5.6851 | 102.3754 | 7.9315 | 192.3958 | 3.1103 | 83.6647 | 78.3128 | 129.845 | 39.4032 | 127.0423 | 121.705 | 152.2737 | 245.757 |  |  | 238.2785 | 300 | 385.4599 | 39.5367
15.5514 | 17.7011 | 27.4 | 10.1158 | 23.3647 | 36.147 | 38.3988 | 23.4525 | 87.2123 | 7.2925 | 97.7677 | 8.9249 | 168.7312 | 3.9832 | 80.7236 | 102.176 | 120.825 | 60.2708 | 122.4584 | 166.879 | 151.0798 | 284.959 |  |  |  |  | 377.7269 | 45.3942
13.9622 | 21.6785 | 25.9 | 11.8798 | 21.7681 | 47.0154 | 34.9691 | 31.0134 | 78.4409 | 9.2706 | 92.0864 | 10.0627 | 149.3467 | 5.0277 | 77.5272 | 139.6368 | 113.6408 | 79.826 | 120.2333 | 219.767 | 151.1767 | 300 |  |  |  |  | 370.1477 | 52.5755
12.4204 | 27.5049 | 23.5279 | 14.5682 | 20.6101 | 58.5503 | 32.4373 | 40.047 | 70.7637 | 11.9394 | 86.5742 | 12.0112 | 136.2058 | 6.0447 | 75.3186 | 181.284 | 108.6928 | 100.77 | 119.5795 | 251.7677 | [6 empty] | 358.32 | 64.5996
10.9981 | 35.5166 | 21.25 | 18.5014 | 19.3791 | 74.6718 | 29.9504 | 53.5641 | 65.2578 | 14.952 | 80.275 | 14.8923 | 122.235 | 7.9522 | 73.3409 | 246.777 | 105.7459 | 121.007 | 119.3672 | 300 | [6 empty] | 345.1956 | 84.1099
9.9883 | 45.0817 | 19.2733 | 23.4423 | 18.5176 | 95.9248 | 28.3632 | 68.1715 | 60.2406 | 19.3336 | 73.2435 | 19.9224 | 107.9432 | 10.2791 | 72.2911 | 300 | 101.7943 | 151.54 | [8 empty] | 334.2397 | 106.494
8.8647 | 60.9537 | 17.9118 | 28.9001 | 17.6942 | 126.849 | 26.6136 | 91.5597 | 56.506 | 24.2119 | 69.1759 | 24.8745 | 99.1553 | 12.961 |  |  | 97.9672 | 201.3724 | [8 empty] | 323.6305 | 132.622
8.2572 | 77.7475 | 16.4937 | 38.3535 | 17.2217 | 161.275 | 25.436 | 119.954 | 53.5356 | 30.1398 | 65.9382 | 29.8697 | 91.5027 | 16.8231 |  |  | 95.672 | 300 | [8 empty] | 314.4411 | 163.629
7.7625 | 100.914 | 15.5773 | 48.3201 | 16.8002 | 206.108 | 24.5352 | 155.216 | 50.4683 | 38.0099 | 61.8466 | 39.9188 | 85.2213 | 21.1686 | [12 empty] | 307.0632 | 199.187
7.4673 | 126.849 | 14.5434 | 63.5514 | 16.6208 | 256.41 | 23.83 | 196.525 | 47.8147 | 44.7831 | 58.8155 | 50.7975 | 81.0327 | 26.0907 | [12 empty] | 300.3414 | 238.985
7.2498 | 151.705 | 13.8623 | 80.7089 | 16.5838 | 300 | 23.3054 | 248.057 | 45.5613 | 53.5641 | 57.2353 | 60.9375 | 76.8721 | 32.593 | [12 empty] | 293.8331 | 299.9163
7.0223 | 199.187 | 13.2435 | 102.089 |  |  | 23.1092 | 300 | 43.6143 | 65.4069 | 54.8067 | 80.0658 | 73.093 | 41.5673 | [12 empty] | 293.8224 | 300
6.9284 | 252.9298 | 12.8282 | 128.361 |  |  |  |  | 41.5583 | 82.3015 | 53.2108 | 100.871 | 69.8198 | 54.3459
6.9149 | 300 | 12.512 | 161.233 |  |  |  |  | 39.6904 | 106.936 | 52.2592 | 119.563 | 67.3099 | 67.8196
|  | 12.2034 | 205.5891 |  |  |  |  | 38.4335 | 134.141 | 50.971 | 151.086 | 65.4903 | 83.2438
|  | 12.0958 | 248.105 |  |  |  |  | 37.182 | 172.498 | 49.4856 | 202.928 | 63.5729 | 106.054
|  | 11.9891 | 300 |  |  |  |  | 36.2871 | 210.855 | 48.5998 | 248.601 | 62.5698 | 130.85