## 176_151
S&C Power Fuses - Type SMD-1A (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (34.5 and 46 kV)
Very Slow Speed (TCC 176-1-5-1) | [9 empty] | Very Slow Speed (TCC 176-1-5-1)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
23502.3 | 0.016302 | 23502.3 | 0.0164 | 23502.3 | 0.016796 | 23502.3 | 0.017494 | 23404.6 | 0.019065 | 23404.6 | 0.019732 | 23404.6 | 0.021405 | 23404.6 | 0.022706
22922 | 0.016498 | 22513 | 0.016896 | 22535.6 | 0.017201 | 22200 | 0.018203 | 21283 | 0.020364 | 21137.3 | 0.021405 | 21380.7 | 0.023127 | 21577.4 | 0.024323
21500.8 | 0.017099 | 21096.2 | 0.017494 | 21117.3 | 0.017898 | 20782.1 | 0.018997 | 17842.8 | 0.023021 | 17914.5 | 0.024702 | 18287.5 | 0.026506 | 18991.6 | 0.027528
20067.2 | 0.017792 | 19650.2 | 0.018293 | 19689.5 | 0.018698 | 19357.6 | 0.020004 | 15027.4 | 0.026069 | 14628.5 | 0.029964 | 15713.6 | 0.030484 | 16629.8 | 0.03155
18635.8 | 0.018605 | 18230.3 | 0.019092 | 18248.5 | 0.019591 | 17923 | 0.021107 | 12462.1 | 0.030379 | 12062 | 0.036389 | 13098.4 | 0.03683 | 14321.9 | 0.03749
17202.9 | 0.019494 | 16795 | 0.020104 | 16828.6 | 0.020691 | 16495.3 | 0.022403 | 10305.2 | 0.036348 | 10112.3 | 0.044041 | 11267.8 | 0.043714 | 12548 | 0.04399
15785.3 | 0.020406 | 15364.7 | 0.021191 | 15395.5 | 0.021897 | 15060.5 | 0.023992 | 8560.73 | 0.044446 | 8600.03 | 0.053484 | 9577.16 | 0.053822 | 11177.8 | 0.051175
14354.6 | 0.021509 | 13930.3 | 0.022403 | 13972.2 | 0.023311 | 13627.2 | 0.025899 | 7222.32 | 0.054411 | 7474.68 | 0.064065 | 8290.67 | 0.065438 | 10129.7 | 0.058519
12923.7 | 0.022807 | 12504.2 | 0.023897 | 12541.8 | 0.024989 | 12195.4 | 0.028209 | 6142.18 | 0.06707 | 6594.01 | 0.07617 | 7267.94 | 0.07956 | 8956.75 | 0.069576
11496.7 | 0.024401 | 11079.1 | 0.025694 | 11101.2 | 0.02711 | 10773.1 | 0.031186 | 5167.08 | 0.084689 | 5773.96 | 0.092449 | 6262.9 | 0.099201 | 7896.93 | 0.083723
10064.9 | 0.026288 | 9650.93 | 0.028014 | 9679.93 | 0.029793 | 9337.63 | 0.035204 | 4455.11 | 0.10481 | 5047.23 | 0.11337 | 5289.79 | 0.12957 | 7087.17 | 0.098408
8628.31 | 0.028689 | 8215.7 | 0.030908 | 8248.63 | 0.033498 | 8998.44 | 0.036486 | 3767.2 | 0.13464 | 4647.88 | 0.1292 | 4597.6 | 0.16257 | 6324.14 | 0.11774
7199.7 | 0.031907 | 6787.19 | 0.035204 | 6814.39 | 0.038919 | 8491.35 | 0.038496 | 3272.37 | 0.16682 | 4159.36 | 0.15493 | 3945.98 | 0.20956 | 5718.05 | 0.13823
5772.06 | 0.036486 | 5354.97 | 0.041805 | 6659.44 | 0.039582 | 7893.54 | 0.041186 | 2712.2 | 0.2259 | 3765.04 | 0.18253 | 3523.16 | 0.25669 | 5140.53 | 0.16464
4340.61 | 0.044284 | 5222.75 | 0.042686 | 6417.54 | 0.040901 | 7243.03 | 0.044904 | 2299.98 | 0.29793 | 3431.6 | 0.21295 | 3108.05 | 0.32245 | 4576.59 | 0.19982
4250.4 | 0.044993 | 5007.93 | 0.044108 | 6092.34 | 0.042813 | 6706.23 | 0.048618 | 2018.57 | 0.37814 | 3027.28 | 0.2637 | 2789.35 | 0.39226 | 4180.84 | 0.2334
4137.17 | 0.045896 | 4716.27 | 0.046308 | 5726.06 | 0.045083 | 6080.16 | 0.053909 | 1707.86 | 0.51322 | 2696.72 | 0.32375 | 2520.58 | 0.4742 | 3872.14 | 0.26781
3982.9 | 0.047191 | 4441.6 | 0.048715 | 5349.62 | 0.04809 | 5573.52 | 0.059599 | 1488.63 | 0.6642 | 2377.63 | 0.40692 | 2310.54 | 0.55801 | 3541.35 | 0.3128
3758.45 | 0.049397 | 4116.54 | 0.052016 | 4938.3 | 0.051809 | 5068.39 | 0.066612 | 1337.52 | 0.81686 | 2126.5 | 0.50216 | 2103.5 | 0.66534 | 3229.57 | 0.37063
3518.39 | 0.052119 | 3830.55 | 0.055595 | 4540.41 | 0.056374 | 4674.01 | 0.073789 | 1170.51 | 1.0529 | 1906.27 | 0.61899 | 1891.05 | 0.81732 | 2948.61 | 0.43915
3296.96 | 0.055101 | 3500.84 | 0.060493 | 4216.53 | 0.060916 | 4182.93 | 0.085136 | 1032.6 | 1.3387 | 1728.51 | 0.747 | 1705.91 | 1.0029 | 2687.47 | 0.52572
3083.29 | 0.058426 | 3189.93 | 0.066612 | 3892.33 | 0.066282 | 3857.46 | 0.094683 | 908.338 | 1.7355 | 1561.96 | 0.9171 | 1549.49 | 1.2263 | 2469.17 | 0.61687
2849.07 | 0.062696 | 2906.63 | 0.073423 | 3665.65 | 0.070914 | 3578.72 | 0.10509 | 799.483 | 2.2771 | 1345.97 | 1.2419 | 1405.81 | 1.503 | 2258.24 | 0.73301
2648.49 | 0.067211 | 2635.28 | 0.082064 | 3459.08 | 0.076096 | 3306.87 | 0.11804 | 717.093 | 2.8985 | 1190.79 | 1.6118 | 1284.25 | 1.8253 | 2048.84 | 0.89222
2459.57 | 0.072409 | 2415.69 | 0.090995 | 3167.68 | 0.084462 | 2998.15 | 0.1366 | 643.193 | 3.7426 | 1067.46 | 2.0434 | 1179.93 | 2.2179 | 1892.13 | 1.0433
2300.17 | 0.0777 | 2170.55 | 0.10426 | 2857.63 | 0.096105 | 2784.29 | 0.15374 | 569.689 | 5.0592 | 970.7 | 2.5202 | 1074.2 | 2.7136 | 1741.42 | 1.2334
2131.82 | 0.084378 | 2003.66 | 0.11607 | 2585.68 | 0.11022 | 2534.48 | 0.17951 | 518.049 | 6.5213 | 875.663 | 3.1859 | 978.51 | 3.3316 | 1588.11 | 1.4765
1989.68 | 0.091266 | 1825.71 | 0.13154 | 2309.39 | 0.1287 | 2309.39 | 0.20877 | 473.251 | 8.498 | 799.941 | 3.9542 | 898.512 | 4.0575 | 1443.32 | 1.8117
1805.74 | 0.10251 | 1698.88 | 0.14572 | 2081.27 | 0.15027 | 2100.08 | 0.2462 | 433.318 | 11.4088 | 714.634 | 5.2633 | 826.472 | 4.9787 | 1299.78 | 2.268
1640.44 | 0.11595 | 1591.96 | 0.15998 | 1896.43 | 0.17321 | 1936.68 | 0.28406 | 398.12 | 16.3414 | 652.837 | 6.7301 | 758.47 | 6.2255 | 1194.2 | 2.737
1471.02 | 0.13378 | 1468.09 | 0.18095 | 1719.39 | 0.20164 | 1777.08 | 0.332 | 375.541 | 21.8385 | 598.436 | 8.6851 | 699.257 | 7.7802 | 1082.84 | 3.4108
1333.7 | 0.1539 | 1357.92 | 0.20446 | 1584.02 | 0.23035 | 1629 | 0.38881 | 356.683 | 29.0513 | 561.595 | 10.608 | 649.111 | 9.712 | 997.741 | 4.1469
1223.79 | 0.1739 | 1241.04 | 0.2359 | 1447.67 | 0.26762 | 1491.76 | 0.45669 | 342.478 | 39.4518 | 511.565 | 14.6807 | 614.755 | 11.7136 | 908.338 | 5.2723
1139.91 | 0.19417 | 1160.61 | 0.26419 | 1325.72 | 0.31093 | 1341.72 | 0.55817 | 329.214 | 56.7358 | 478.7 | 18.967 | 585.224 | 14.0873 | 848.038 | 6.3081
1049.11 | 0.22049 | 1078.9 | 0.29793 | 1193.57 | 0.37329 | 1222.56 | 0.66612 | 318.829 | 81.6855 | 445.135 | 25.7721 | 550.771 | 18.2107 | 799.483 | 7.4657
957.855 | 0.25491 | 991.975 | 0.34409 | 1102.9 | 0.43069 | 1087.57 | 0.82718 | 311.255 | 117.472 | 422.783 | 32.6727 | 520.426 | 23.4468 | 753.278 | 9.051
869.303 | 0.29912 | 912.049 | 0.39858 | 1009.99 | 0.50388 | 990.983 | 0.99307 | 307.008 | 169.034 | 406.642 | 43.2898 | 497.986 | 29.0513 | 719.972 | 10.4991
809.719 | 0.33698 | 829.389 | 0.47332 | 922.137 | 0.59421 | 903.877 | 1.191 | 302.819 | 248.155 | 392.913 | 58.4855 | 475.968 | 37.1905 | 681.865 | 12.7577
740.765 | 0.39269 | 767.152 | 0.54394 | 862.376 | 0.67478 | 812.152 | 1.4864 | 300.058 | 349.585 | 382.483 | 81.3119 | 461.216 | 45.5028 | 646.885 | 15.7439
672.955 | 0.46401 | 699.72 | 0.64528 | 804.071 | 0.77315 | 742.991 | 1.7898 | 298.858 | 460.273 | 374.039 | 109.728 | 447.178 | 61.6517 | 614.755 | 19.608
619.352 | 0.53696 | 625.577 | 0.79259 | 748.21 | 0.89116 | 678.361 | 2.181 | 298.175 | 566.708 | 367.671 | 146.555 | 440.32 | 80.7084 | 582.884 | 25.3473
575.748 | 0.6128 | 558.732 | 0.98717 | 697.624 | 1.0241 | 631.865 | 2.5465 | 298.516 | 599.102 | 364.318 | 190.76 | 433.318 | 104.272 | 561.595 | 31.5865
527.773 | 0.71836 | 510.13 | 1.1769 | 647.861 | 1.1863 | 582.699 | 3.0391 |  |  | 360.997 | 262.19 | 429.368 | 136.034 | 534.006 | 45.7119
492.583 | 0.81657 | 468.558 | 1.3962 | 605.875 | 1.3579 | 542.218 | 3.591 |  |  | 358.936 | 372.545 | 426.185 | 177.268 | 518.939 | 61.6517
458.362 | 0.93654 | 426.945 | 1.6946 | 568.88 | 1.5528 | 508.601 | 4.1846 |  |  | 357.297 | 453.986 | 424.723 | 224.733 | 506.902 | 82.1079
420.168 | 1.111 | 393.331 | 2.0084 | 534.679 | 1.7703 | 475.165 | 4.9397 |  |  | 356.275 | 556.729 | 423.509 | 303.271 | 496.847 | 114.941
384.387 | 1.3207 | 362.001 | 2.3968 | 501.029 | 2.0406 | 443.039 | 5.9127 |  |  | 356.683 | 606.356 | 423.509 | 375.116 | 492.881 | 149.954
349.899 | 1.595 | 332.169 | 2.9005 | 466.688 | 2.3921 | 416.403 | 7.0213 |  |  |  |  | 423.025 | 463.715 | 488.947 | 192.296
323.643 | 1.8772 | 306.323 | 3.4925 | 442.596 | 2.6922 | 387.475 | 8.539 |  |  |  |  | 423.752 | 563.147 | 486.156 | 246.737
306.016 | 2.1086 | 284.472 | 4.1597 | 418.909 | 3.0664 | 367.105 | 10.0398 |  |  |  |  | 423.752 | 606.356 | 483.658 | 329.737
283.336 | 2.4693 | 269.248 | 4.7614 | 398.08 | 3.4683 | 346.764 | 12.1012 | [6 empty] | 482.828 | 422.361
260.507 | 2.9675 | 255.604 | 5.4286 | 379.043 | 3.9113 | 328.535 | 14.528 | [6 empty] | 482.828 | 530.565
239.997 | 3.5661 | 244.112 | 6.2138 | 363.452 | 4.3284 | 315.021 | 17.1325 | [6 empty] | 482.276 | 600.477
222.655 | 4.2306 | 231.742 | 7.2553 | 348.503 | 4.8281 | 302.971 | 20.0042
208.433 | 5.0039 | 221.323 | 8.4043 | 333.834 | 5.434 | 289.06 | 25.3142
195.12 | 5.8951 | 212.219 | 9.6967 | 321.064 | 6.0674 | 277.171 | 31.4661
184.678 | 6.8355 | 203.287 | 11.2436 | 304.49 | 7.0283 | 267.637 | 38.2295
174.445 | 7.9971 | 195.511 | 13.0113 | 293.136 | 7.832 | 259.727 | 46.5852
168.276 | 8.8675 | 188.786 | 15.057 | 282.205 | 8.7885 | 251.295 | 58.7173
162.164 | 9.8815 | 182.11 | 17.6683 | 272.226 | 9.9702 | 243.624 | 76.1718
157.056 | 11.0005 | 175.846 | 20.815 | 261.29 | 11.5034 | 236.66 | 100
151.2 | 12.8061 | 170.478 | 24.5709 | 250.543 | 13.3783 | 231.51 | 128.699
146.584 | 14.6731 | 166.602 | 28.4341 | 243.137 | 15.042 | 227.153 | 166.13
140.134 | 17.9692 | 162.326 | 34.3746 | 236.897 | 17.0138 | 223.771 | 214.873
136.264 | 20.6093 | 159.59 | 40.2161 | 229.666 | 19.6497 | 220.219 | 284.058
131.841 | 24.4978 | 157.056 | 47.4728 | 223.547 | 22.6264 | 216.723 | 386.879
128.2 | 28.947 | 154.254 | 57.334 | 217.81 | 26.2619 | 214.781 | 502.383
125.16 | 34.0686 | 151.958 | 69.2436 | 213.07 | 30.3004 | 214.352 | 600.146
122.559 | 40.0964 | 150.295 | 82.8004 | 208.642 | 35.0295
120.372 | 47.0503 | 148.502 | 104.26 | 204.306 | 40.8604
118.107 | 57.5622 | 146.584 | 130.761 | 200.26 | 47.7092
116.465 | 68.8321 | 144.836 | 182.027 | 196.687 | 56.8802
114.731 | 82.0635 | 142.965 | 254.15 | 193.372 | 67.8815
113.136 | 99.9007 | 141.826 | 339.335 | 190.112 | 81.1717
111.898 | 126.796 | 140.836 | 471.907 | 186.721 | 100
110.895 | 172.349 | 140.274 | 584.844 | 183.941 | 120.892
110.342 | 220.276 | 140.134 | 600.146 | 181.202 | 154.509
109.682 | 279.857 |  |  | 179.04 | 188.655
109.135 | 342.043 |  |  | 176.375 | 239.445
108.699 | 445.487 |  |  | 174.794 | 290.334
108.591 | 573.34 |  |  | 172.537 | 391.518
108.591 | 600.146 |  |  | 171.333 | 540.166
|  |  |  | 170.991 | 600.146